## Sheet1
BRANXTON WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2023-2024
| Environment Protection Licence No. 1680 |  |  |  | Hunter Water Corporation
| Date Obtained: 1 October 2024 |  |  |  | 36 Honeysuckle Drive
| Date Published: 18 March 2025 |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Outlet to Farmers Reuse Storage
Site Code 5SL0500
|  |  | No. of times measured during the year for licence reporting* | Annual Summary
1 October 2023 to 30 September 2024
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | First 24hrs then weekly | - | - | - | 5 | - | 10 | - | N/A | N/A | N/A | N/A | Yes
Chlorine (total residual) | milligrams per litre | First 24hrs then weekly | - | - | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Enterococci | colony forming units per 100 mL | First 24hrs then weekly | - | - | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | First 24hrs then weekly | - | - | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate+Nitrite (oxidised nitrogen) | milligrams per litre | First 24hrs then weekly | - | - | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | milligrams per litre | First 24hrs then weekly | - | - | - | 7.5 | - | 10 | - | N/A | N/A | N/A | N/A | Yes
Nitrogen (Ammonia) | milligrams per litre | First 24hrs then weekly | - | - | - | 1 | - | 3 | - | N/A | N/A | N/A | N/A | Yes
pH | pH | First 24hrs then weekly | - | - | - | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | - | Yes
Phosphorus (total) | milligrams per litre | First 24hrs then weekly | - | - | - | 0.3 | - | 1 | - | N/A | N/A | N/A | N/A | Yes
Total Kjeldahl Nitrogen | milligrams per litre | First 24hrs then weekly | - | - | - | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | First 24hrs then weekly | - | - | - | 10 | - | 20 | - | N/A | N/A | N/A | N/A | Yes
* No samples were collected as no discharge through EPL point 1 occurred during the Annual Return period
EPA Id. No. 11 | Site Description - Discharge to Black Creek from Reuse Water Storage
Site Code 5BL0500
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2023 to 30 September 2024
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Chlorine (total residual) | milligrams per litre | First 24hrs then weekly | 39 | <0.1 | 0.3 | N/A | N/A | 0.5 | 0.22 | N/A | N/A | N/A | N/A | Yes
EPA Id. No. 12 | Site Description - Reuse Water Pump Station
Site Code 5SK0535
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2023 to 30 September 2024
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Weekly | 52 | <2 | 3 | 5 | <2 | 10 | <2 | N/A | N/A | N/A | N/A | Yes
Faecal Coliforms | colony forming units per 100 mL | Weekly | 52 | <1 | ~5 | 150 | <1 | 200 | <1 | N/A | N/A | N/A | N/A | Yes
Enterococci | colony forming units per 100 mL | Weekly | 52 | <1 | <1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate+Nitrite (oxidised nitrogen) | milligrams per litre | Monthly | 12 | 2.15 | 6.52 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | milligrams per litre | Monthly | 12 | 2.35 | 10.12 | 7.5 | 4.49 | 10 | 8.26 | N/A | N/A | N/A | N/A | Yes
Nitrogen (ammonia) | milligrams per litre | Monthly | 12 | <0.05 | 2.66 | 1 | 0.07 | 3 | 2.3 | N/A | N/A | N/A | N/A | Yes
pH | pH | Weekly | 52 | 6.88 | 7.48 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.88 - 7.48 | Yes
Phosphorus (total) | milligrams per litre | Monthly | 12 | 0.016 | 0.358 | 0.3 | 0.049 | 1 | 0.322 | N/A | N/A | N/A | N/A | Yes
Total Kjeldahl Nitrogen | milligrams per litre | Monthly | 12 | <0.1 | 4.1 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Weekly | 52 | <1 | 5 | 10 | <1 | 20 | 2 | N/A | N/A | N/A | N/A | Yes
EPA Id. No. 13 | Site Description - Outlet to Anvil Creek from Wet Weather Storage Pond
Site Code 5OV0410
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2023 to 30 September 2024
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | First 24hrs then weekly | 2 | 9 | 16 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Enterococci | colony forming units per 100 mL | First 24hrs then weekly | 2 | ~100 | ~130000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | First 24hrs then weekly | 2 | 21000 | 230000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrate+Nitrite (oxidised nitrogen) | milligrams per litre | First 24hrs then weekly | 2 | 3.08 | 3.49 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | milligrams per litre | First 24hrs then weekly | 2 | 6.69 | 7.71 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
pH | pH | First 24hrs then weekly | 2 | 7.06 | 7.13 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | milligrams per litre | First 24hrs then weekly | 2 | 1.09 | 1.22 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Kjeldahl Nitrogen | milligrams per litre | First 24hrs then weekly | 2 | 8.8 | 10.9 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | First 24hrs then weekly | 2 | 51 | 56 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
**No samples were collected as no discharge through EPL point 13 occurred during the Annual Return period |  |  | 0 | - | -
VOLUME MONITORING
Annual Summary
1 October 2023 to 30 September 2024
Monitoring Point |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Anvil Creek Discharge |  | kilolitres per day | Continuous during discharge | 366 |  | 0 | 0 | 0 | 31104 | Yes
Point 2 - Woodlot Discharge |  | kilolitres per day | Continuous | 366 |  | 0 | 0 | 0 | N/A | N/A
Point 6 - Farmer Discharge |  | kilolitres per day | Continuous | 366 |  | 0 | 0 | 0 | N/A | N/A
Point 8 - Spillway to Anvil Creek from Wet Weather Pond |  | kilolitres per day | Continuous during discharge | 366 |  | 0 | 0 | 0 | N/A | N/A
Point 9 - Spillway to Anvil Creek from Farmer's Reuse Storage |  | kilolitres per day | Continuous | 366 |  | 0 | 0 | 0 | N/A | N/A
Point 10 - Vintage Golf Course |  | kilolitres per day | Continuous | 366 |  | 0 | 572 | 3022 | N/A | N/A
Point 11 - Black Creek Discharge |  | kilolitres per day | Continuous | 366 |  | 0 | 982 | 5785 | 31104 | Yes
Point 13 - Outlet to Anvil from Wet Weather Storage |  | kilolitres per day | Continuous during discharge | 366 |  | 0 | 2 | 408 | N/A | N/A
Point 14 - Branxton Golf Course |  | kilolitres per day | Continuous | 366 |  | 0 | 31 | 347 | N/A | N/A
Combined Point 1, 8, 9, 11 and 13 |  | kilolitres per day | Continuous | 366 |  | 0 | 984 | 5902 | 31104 | Yes