## Karuah
KARUAH WASTEWATER TREATMENT WORKS - ANNUAL POLLUTION MONITORING SUMMARY - 2022-2023
| Environment Protection Licence No. 10230 |  |  |  | Hunter Water Corporation
| Date Obtained: 4 October 2023 |  |  |  | 36 Honeysuckle Drive
| Date Published: 6 March 2024 |  |  |  | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 | Site Description - Flow meter on discharge line from effluent irrigation pump
Site Code 5SL3000
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2022 - 30 September 2023
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Quarterly | 4 | <2 | 8 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Nitrogen (Total) | milligrams per litre | Quarterly | 4 | 0.8 | 3.5 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | milligrams per litre | Quarterly | 4 | 0.07 | 0.21 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Quarterly | 4 | <1 | 23 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 2 | Site Description - Overflow discharge pit
Site Code 5OV3000
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2022 - 30 September 2023
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | First 24 hrs then weekly | 16 | <2 | 4 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Faecal Coliforms | colony forming units per 100 mL | First 24 hrs then weekly | 16 | ~9 | 4700 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | First 24 hrs then weekly | 16 | <1 | 7 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
EPA Id. No. 3 | Site Description - Discharge from the UV disinfection plant to the effluent storage dam
Site Code 5EE3000
|  |  | No. of times measured during the year for licence reporting | Annual Summary
1 October 2022 - 30 September 2023
| Unit of | Sampling |  |  |  | 50%ile | 50%ile | 90%ile | 90%ile | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant | Measurement | Frequency |  | Minimum | Maximum | Limit | Actual | Limit | Actual | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | milligrams per litre | Monthly | 12 | <2 | 5 | N/A | N/A | 15 | 4 | N/A | N/A | 20 | 5 | Yes
Faecal Coliforms | colony forming units per 100 mL | Monthly | 12 | <2 | ~60 | N/A | N/A | 200 | 15 | N/A | N/A | 500 | ~60 | Yes
Nitrogen (ammonia) | milligrams per litre | Monthly | 12 | 0.27 | 1.14 | N/A | N/A | 3 | 0.81 | N/A | N/A | 5 | 1.14 | Yes
Nitrogen (Total) | milligrams per litre | Monthly | 12 | 4.6 | 18.6 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Phosphorus (Total) | milligrams per litre | Monthly | 12 | 0.36 | 1.55 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | milligrams per litre | Monthly | 12 | <1 | 8 | N/A | N/A | 20 | 8 | N/A | N/A | 30 | 8 | Yes
pH | pH | Monthly | 12 | 6.8 | 7.3 | N/A | N/A | N/A | N/A | N/A | N/A | 6.5 - 8.5 | 6.80 - 7.30 | Yes
VOLUME MONITORING
Annual Summary
1 October 2022 - 30 September 2023
Monitoring Point |  | Unit of | Sampling | No. of times measured during the year |  |  |  |  | Volume | Within
|  | Measurement | Frequency |  |  | Minimum | Mean | Maximum | Limit | Limits?
Point 1 - Effluent Irrigation |  | kilolitres per day | Daily | 365 |  | 0 | 248 | 2466 | 3000 | Yes
Point 2 - Overflow Discharge |  | kilolitres per day | Daily | 365 |  | 0 | 111 | 4915 | N/A | N/A