## Kearsley
KEARSLEY WASTEWATER TREATMENT WORKS - MONTHLY POLLUTION MONITORING SUMMARY - FEBRUARY 2025
|  | Environment Protection Licence No. 3232 | [6 empty] | Licensee | Hunter Water Corporation
|  | Date Obtained: 3 March 2025 | [7 empty] | 36 Honeysuckle Drive
|  | Date Published: 20 March 2025 | [7 empty] | NEWCASTLE WEST NSW 2302
QUALITY MONITORING
EPA Id. No. 1 |  | Site Description - No.2 oxidation pond to tailings dams for evaporation and discharge to Swamp Creek tributary
Site Code 5SL2600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2025 to 28 February 2025
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 3 | 13.25 | 13.5 | 23 | N/A | N/A | 60 | 23 | Yes*
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 4 | 323 | 530.25 | 334 | 1130 | N/A | N/A | N/A | N/A | N/A
Enterococci | Ent Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | ~500 | ~500 | ~500 | ~500 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.1 | 0.1 | 0.1 | 0.1 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 6.95 | 6.95 | 6.95 | 6.95 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Oxidised nitrogen | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 9.26 | 9.8575 | 9.985 | 10.2 | N/A | N/A | N/A | N/A | N/A
Phosphorus (dissolved reactive) | RP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.81 | 0.81 | 0.81 | 0.81 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 2.51 | 2.51 | 2.51 | 2.51 | N/A | N/A | N/A | N/A | N/A
Total Kjedahl Nitrogen | TKN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 6.9 | 6.9 | 6.9 | 6.9 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 58 | 108.5 | 72.5 | 231 | N/A | N/A | 70 | 231 | Yes*
*The licensee is not taken to have exceeded a quality limit specified in this licence for pH, BOD or TSS if the licensee shows that the level of chlorophyll-a in the oxidation ponds during any exceedance was 100 ug/L or more (showing that the exceedance was caused by excessive algal growth).
EPA Id. No. 2 |  | Site Description - Tailings Dam discharge from the premises to Swamp Creek
Site Code 5MF2600
[6 empty] | No. of times measured during the month for licence reporting | Monthly Summary
1 February 2025 to 28 February 2025
|  | Unit of |  | Sampling |  |  |  | Mean | Median |  | 3DGM | 3DGM | 100%ile | 100%ile | Within
Pollutant |  | Measurement |  | Frequency |  |  | Minimum | Value | Value | Maximum | Limit | Actual | Limit | Actual | Limits
Biochemical Oxygen Demand | BOD | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 8 | 10 | 10.5 | 11 | N/A | N/A | N/A | N/A | N/A
Chlorophyll a | Chlorophyll a | micrograms per litre | (ug/L) | Weekly | WEEKLY | 4 | 99.1 | 225.275 | 239.5 | 323 | N/A | N/A | N/A | N/A | N/A
Enterococci | Ent Hdn | colony forming units per 100 mL | CFU/100mL | Monthly | MONTHLY | 1 | ~80 | ~80 | ~80 | ~80 | N/A | N/A | N/A | N/A | N/A
Nitrogen (ammonia) | Ammonia | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 0.21 | 0.21 | 0.21 | 0.21 | N/A | N/A | N/A | N/A | N/A
Nitrogen (total) | Total N | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.75 | 5.75 | 5.75 | 5.75 | N/A | N/A | N/A | N/A | N/A
Oil and Grease | Grease | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <2 | <2 | <2 | <2 | N/A | N/A | N/A | N/A | N/A
Oxidised nitrogen | TON | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | <0.05 | <0.05 | <0.05 | <0.05 | N/A | N/A | N/A | N/A | N/A
pH | pH | pH | pH | Weekly | WEEKLY | 4 | 7.75 | 8.665 | 8.84 | 9.23 | N/A | N/A | N/A | N/A | N/A
Phosphorus (dissolved reactive) | RP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 2.83 | 2.83 | 2.83 | 2.83 | N/A | N/A | N/A | N/A | N/A
Phosphorus (total) | TP | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 3.83 | 3.83 | 3.83 | 3.83 | N/A | N/A | N/A | N/A | N/A
Total Kjedahl Nitrogen | TKN | milligrams per litre | (mg/L) | Monthly | MONTHLY | 1 | 5.7 | 5.7 | 5.7 | 5.7 | N/A | N/A | N/A | N/A | N/A
Total Suspended Solids | TSS | milligrams per litre | (mg/L) | Weekly | WEEKLY | 4 | 29 | 49.25 | 36 | 96 | N/A | N/A | N/A | N/A | N/A
Note: For pollutants with less than four samples measured during the monthly period see below for interpretation of summary tables: One required sample for licence reporting: Min, Mean, Median and Max values are all the exact data point Two required samples for licence reporting: Min and Max values are the two exact data points Three required samples for licence reporting: Min, Median and Max values are the three exact data points
VOLUME MONITORING |  |  | 37
Monthly Summary
1 February 2025 to 28 February 2025
Monitoring Point |  |  | Flow Column | Unit of |  | Sampling | No. of times measured during the month |  | Minimum | Mean | Maximum | Volume | Within Limits
|  |  |  | Measurement |  | Frequency | [5 empty] | Limit
Point 1 - No.2 oxidation pond to tailings dams for evaporation and discharge to Swamp Creek tributary |  |  | 7 | kilolitres per day | 0.80514 | Continuous | 28 |  | 27.952 | 156.6544 | 1096.054 | 2500 | Yes
Point 2 - Tailings Dam discharge from the premises to Swamp Creek |  |  | 7 | kilolitres per day | 0.80514 | Continuous during discharge | 28 |  | 1 | 1.4286 | 9 | N/A | N/A
Chlorophyll 'a'
Chlorophyll 'a'
15500
N/A
N/A
Note on D55: awebb: Last row of flow table